## Slide 1: Reducing NRW with AI-Powered Technologies

## Slide 2: House Keeping Rules
Mute Your Mic – Please keep your microphone muted unless speaking to minimize background noise.
Q&A Session – There will be a dedicated Q&A session at the end of the webinar. Feel free to submit questions via the Q&A feature.
Stay Engaged – Polls, reactions, and the chat are great ways to participate.
Recording & Replay – This webinar is being recorded. Recording & slides will be shared afterward.
Tech Support – If you experience any issues, message our tech support team in the chat.

## Slide 3: Enable translated captions

## Slide 4
Kate Stanton-Davies
Co-founder and Director of
Water Loss Research & Analysis
Katesdavies@wlranda.com
www.wlranda.com
8 years of experience in NRW reduction software and training

## Slide 5
Baker Bozeyeh
Co-founder and CEO of Flowless
www.flowless.co
Business development & expansion leader

## Slide 6: Agenda
Introduction
Understanding NRW Fundamentals
Building an NRW Strategy for 2025
Leveraging Technology for NRW Reduction
Case Studies
Q&A Session
Closing & Call-to-Action

## Slide 7: Introduction
Importance of NRW Reduction
  Significant loss for water utilities in operational costs and environmental sustainability
  Critical for meeting community needs and preserving resources
Impact of NRW Reduction
  Affects utility performance, customer satisfaction, and community trust
  Enhances service delivery and operational efficiency
Webinar Goals
  Understand core components of NRW and real losses developments over the last 30 years
  Explore strategies to reduce NRW using AI-powered technologies
  Implement sustainable and actionable strategies with Flowless' solutions

## Slide 8: The challenges of global water stress
Growing populations
Climate change
Increasing demand - agriculture, industry, manufacturing, energy production, datacenters, AI
Ageing infrastructure
Lack of capital investment

## Slide 9: Linking NRW reduction to lower carbon emissions
  Energy is used to extract, treat, pump and distribute each unit of water.
  Every unit of water lost to leakage results in carbon emissions that would otherwise be avoided if such leakage were reduced.
  Must be balanced against carbon expended in activities to reduce NRW
  IWA Leakage Emissions Initiative, including carbon water balances - Home | LEI Group

## Slide 10: Time to get back to the basics
Let's review some fundamentals before we look at setting strategy and exploring solutions
Focus on Real Losses

## Slide 11: Poll 1
Notes: First, a quick poll to understand how much you already know about NRW – please answer the poll question coming up on screen now.

## Slide 12: Understanding NRW Fundamentals
“You can’t connect the dots looking forward; you can only connect them looking backwards.” – Steve Jobs
“Study the past if you would define the future.” – Confucius

## Slide 13: NRW Milestones from the last 30 years
1994
Component Analysis of Real Losses (BABE)
Fixed and Variable Area Discharges (FAVAD)
1999
IWA Water Balance,
IWA recommended (KPIs) for NRW and Real Losses
Unavoidable Annual Real Losses UARL, and Infrastructure Leakage Index ILI
2017
Variable N1 Concept
2020
UARL with SCF
1997
Night Flow Component Analysis
Average Zone Point and Night Day Factors
2015
EU Reference Document
Good Practices on Leakage Management
2012
Pressure:bursts relationship
2000-2001
Economic Intervention Policy for Active Leakage Control based on rate of Rise of Unreported Leakage
Use of Confidence Limits in Water Balance and Night Flow calculations

## Slide 14: Let's start with a Water Balance
Non-Revenue Water
Unbilled Authorised Consumption
Apparent (commercial)Losses*
Real (physical) Losses
Reducing each component requires a different approach and set of targeted interventions
*AL-Guidance-Note-Final-15th-Sep-2016-00000002.pdf
Apparent Water Losses – MCAST

## Slide 15: The 4 Basic Methods of Managing Real Losses

## Slide 16: Benefits of managing excess pressure
Managing transients
Reduction of Leak Flow Rates
Reduction of Burst Frequencies
Extension of infrastructure life
Reduction in consumption

## Slide 17: Real Losses KPIs
Based on EU Reference Document
Choose service connection if density >20/km; if not, choose mains, or base choice on country custom and practice

## Slide 18: What is a System Correction Factor?
UARL1999 equation calculates lowest estimate of Annual Real Losses for a well-maintained whole system:-
  More than 5000 service connections
  Average Pressure range 45-60m
  Outside these boundary conditions, it tends to over-estimate volumes for small lower pressure systems and under-estimate for larger higher-pressure systems
A System Correction Factor overcomes these boundary conditions and can be used:-
  For whole system, zone or DMA
  For any number of service connections
  At wide range of Average Pressures
UARL with SCF = SCF x UARL1999 volume
​
Provides Utility with priority insights for leakage reduction and pressure management opportunities​, identifying maximum recoverable leakage for each DMA or Zone

## Slide 19: Why an SCF calculation is different
FAVAD (Fixed and Variable Area Discharges)
  Relationship between how the leak flow area in different pipe materials responds to changes in pressure
  N1 Power Law simplifies this pressure:leak flow rate relationship
  Original UARL equation uses N1=1 for simplicity (10% reduction in pressure results in 10% reduction in leak flow rate)
  SCF calculations use N1=0.5 for rigid pipes and N1=1.5 for flexible pipes and Unavoidable Background Leakage
Poisson effect
  Small, low pressure systems will have less than the average numbers of UARL bursts per year
  Median burst frequencies modelled in SCF calculations
Pressure:bursts
  Original UARL equation used burst frequencies at 50m pressure
  SCF models pressure:bursts relationship across a wide range of operating pressures

## Slide 20: Scenarios for using SCF – Small DMA, Low Pressure
EXAMPLE
Number of service connections=3000
Average length of private service pipe = 3m/conn (from curb stop to meter)
Mains Length = 50 km
Average Zone Pressure = 35m
60% rigid mains
40% rigid services (mains to curb stop)
30% rigid services (curb stop to meter)
SCF result | UARL1999 volume in m3/day | UARL with SCF volume in m3/day
0.74 | 123.4 | 91.0
Current Target
New Target

## Slide 21: Scenarios for using SCF – Small DMA, Low Pressure
In this example, if AZP can be reduced by 1 m (from 35m to 34m)
UARL volume can be reduced by 3.6m3/day or 1314m3/year

## Slide 22: Scenarios for using SCF – Large DMA, High Pressure
EXAMPLE
Number of service connections=6000
Average length of private service pipe = 3m/conn (from curb stop to meter)
Mains Length = 100 km
Average Zone Pressure = 70m
60% rigid mains
40% rigid services (mains to curb stop)
30% rigid services (curb stop to meter)
SCF result | UARL1999 volume in m3/day | UARL with SCF volume in m3/day
1.17 | 493.5 | 578.2
Current Target
New Target

## Slide 23
If AZP can be reduced by 1 m (from 70m to 69m),
UARL volume can be reduced by approx. 15m3/day or 5475m3/year
Scenarios for using SCF – Large DMA, High Pressure

## Slide 24: Why should Utilities use SCF?
Use the original 1999 UARL equation to calculate a whole system UARL​
  Consider SCF calculations for Boundary Cases​ (<5000 conns, outside 45-60m Average Pressure range)
Use SCF to map all zones and systems within a Utility for a complete top down/bottom up view of your system ​
  Where can UARL volume targets be reduced? ​
  Where UARL volume targets may not be achievable?​
  Target zones or systems where further pressure management may be possible to reduce bursts, leak flow rates and UARL volumes, with reductions quantified​
Notes: Read the slide

## Slide 25
More than 3000 SCF calculations in 13 countries
"adopt the system level SCF corrected UARL as future targets to plan leakage control works i.e. pressure reduction, sensors, traditional Active Leak Detection or DMA sectorisation."
Sydney Water, Australia
Water Services Corporation,Malta
“With over 55,000 water systems in North America, and over 90% of those designated as ‘small systems’ and many others with abnormally high pressures …These systems can now use the FWAS Version 6 to establish a baseline standing, then engage the UARL with SCF web application to refine their understanding for predictive leakage modeling and quantify the scale of improvement opportunity that exists specifically for their system”
Will Jernigan, USA
“UARL with SCF software allows us to further customise UARL calculations for each of 320 individual Zones and Sub-Zones, for the first time. Integrating this methodology within the snapshot ILl concept will result in rapid identification of Zones where we may expect to set and achieve lower leakage targets and better quantification of leakage and burst reductions from further pressure management. Fine tuning the UARL now is allowing us further scope to further reduce leakage, saving millions of euros in the process.”
Water Services Corporation, Malta

## Slide 26: Where will the journey take us now?
Stand on the strong foundations built by the pioneers of water loss reduction over the last 30 years
Wherever you are on you NRW reduction journey, there are proven conceptual data-driven and AI solutions to help you move forward
Whatever solution you use, make sure you understand the fundamentals first!

## Slide 27: Building A Comprehensive NRW Strategy
Start small, gain traction, and scale-it up!

## Slide 28: Poll 2

## Slide 29
High Cost Inefficiency
emerging water leaks
limited team capacity
Falling behind regulatory targets
Disrupted water service delivery
budget limitations
aging infrastructure
Surface-level problems
Root causes
low data accuracy
manual data handling

## Slide 30: Tackling The Root Causes
Limited capacity
Poor insights
Budget constraints
Aging infrastructure
Efficient operations & supply continuity

## Slide 31: Losses Lifecycle Management
The
Comprehensive Approach
Is it a leak? Or is it something else?
Awareness
Quantify
(How big is it?)
Locate
(Where is it?)
Prioritize (tackling the low hanging fruit)
Take action
(How to deal with it)
Evaluate & Iterate

## Slide 32: Leveraging Technology
For effective NRW Management

## Slide 33: Technology is not a magical wand!
Said by a wise NRW guru!

## Slide 34: Paradigm Shift
Data-driven approach
Insight-driven approach

## Slide 35: Poll 3

## Slide 36: It’s NOT Only About Data Collection!
Step
01
Step
02
Step
03
Step
04
Step
05
Data Collection
Intervention Planning
Tracking & Evaluation
Data Analysis
Implementation

## Slide 37: Smooth Tech Adoption Journey

## Slide 38: Step 1: Understand The Needs
At the right frequency for accurate & timely insights
Accurate Data Collection

## Slide 39: Intervention Planning
go to the field, understand the context

## Slide 40: Collect & Field Data
Ideally in real-time

## Slide 41: Step 2: Set your targets
based on measurable & attainable targets
Define priorities
At the right frequency for accurate & timely insights
Accurate Data Collection

## Slide 42: Step 3: Watch & Analyze
to spot unusual events & predict issues before they emerge
Keep an eye on the analytics
based on measurable & attainable targets
Define priorities
At the right frequency for accurate & timely insights
Accurate Data Collection

## Slide 43: Step 4: Tackle The Low-Hanging Fruit
to allocate resources to the exact source of problem
Utilize The Insights
to spot unusual events & predict issues before they emerge
Keep an eye on the analytics
based on measurable & attainable targets
Define priorities
At the right frequency for accurate & timely insights
Accurate Data Collection

## Slide 44: Step 5: Evaluate & Improve
Continuous optimization and improvement
to allocate resources to the exact source of problem
Utilize The Insights
to spot unusual events & predict issues before they emerge
Keep an eye on the analytics
based on measurable & attainable targets
Define priorities
At the right frequency for accurate & timely insights
Accurate Data Collection

## Slide 45: WaterCloud & SCF

## Slide 46: Live Demo!

## Slide 47: Case Studies
Palestine, Malaysia, Brazil, Malta, Quebec, Australia
Notes: This slide presents case studies showcasing how Flowless' integration of SCF has significantly reduced NRW, especially in areas where traditional methods were less effective. Original Content: Case Studies Demonstrating Impact Through case studies, we’ll showcase how Flowless’ integration of SCF has led to substantial reductions in NRW, particularly in areas where traditional methods struggled to make an impact.

## Slide 48: Case Study: Saving 10,000 m3/month
Salfeet Municipality, Palestine

## Slide 49: Case Study 1 - Water Services Corporation (Malta, Europe)
All properties supplied through roof storage tanks
57% of Malta’s potable water produced by 3 reverse osmosis plants; the remainder is pumped from underground aquifers.
130,000 service connections
1330 miles (2,141 km) mains
Average Pressure 45.5 psi (32m ,3.2 bar)
Customer meters are located at the curb stop
93% rigid mains, 5% rigid services (mains to curb stop)
320 UARL with SCF calculations to map all zones and DMAs across 4 regions
Latest ILI 1.8, reduced from ILI of approx. 20 in 2000
All data reproduced with kind permission of
Water Services Corporation, Malta

## Slide 50
All data reproduced with kind permission of Water Services Corporation, Malta
Case Study 1 - Water Services Corporation (Malta, Europe)
Case Study characteristics | 
Zone/System size | 5 – 14,000 service connections
Small Systems | >99% zones have <5,000 service connections
Managed AZP ranges | 24-105 psi (17-74 m)

## Slide 51
Standard UARL equation over-predicts UARL volumes in some zones by 61%-14%
All data reproduced with kind permission of Water Services Corporation, Malta
Case Study 1 - Water Services Corporation (Malta, Europe)
SCFs at current operating pressures range from
0.39 – 0.86
SCF calculation results are being used in conjunction with Snapshot ILI
to rapidly identify zones where lower leakage targets could be set ,
and to better quantify leakage and burst reductions
from further pressure management
Why are these SCFs all < 0.9 ?
A continuous program of Pressure Management over > 20 years
A large percentage (>99%) of small systems with less than 5,000 service connections
Mostly flexible materials on service connections
How are WSC using SCF calculation results?

## Slide 52: Case Study 2 - Quebec Province (Canada)
626 Individual water utilities
2,111,989 service connections
26,000 miles (41,429 km) mains
Average Pressure 70.7 psi (49.7 m)
Overall, 67% rigid mains, 95% rigid services (mains to curb stop), 95% rigid services (curb stop to meter)
855 UARL with SCF calculations to map DMAs and zones across 17 regions
Latest overall ILI 6.6 in 2019
65% of networks (in number, not length) achieved a low or moderate ILI of <4 in 2019
All data reproduced with kind permission of MAMH and
Reseau Environnement, Quebec

## Slide 53: Case Study 2 - Quebec Province (Canada)
All data reproduced with kind permission of MAMH and Reseau Environnement, Quebec
Case Study characteristics | 
Zone/System size | 5 – 377,362 service connections
Small Systems | >88% zones have <5,000 service connections
Managed AZP ranges | 25-145 psi (18-102 m)

## Slide 54: Case Study 2 - Quebec Province (Canada)
For some zones or regions, standard UARL equation
over-predicts UARL volumes by up to 62%
SCFs at current operating pressures range from
0.38 – 1.75
SCF calculation results are being used so that
Quebec Efficiency Strategy has a better understanding of their systems and the way to reach their water loss objectives.
Why are these SCFs so varied ?
A wide variety of system/zone size
Mostly rigid service connections
A wide range of operating pressures
How are SCF calculation results being used?
For some zones or regions, standard UARL equation
under-predicts UARL volumes by up to 75%
A large percentage (>88%) of small systems with less than 5,000 service connections
All data reproduced with kind permission of MAMH and Reseau Environnement, Quebec

## Slide 55: Case Study 3 – Sydney Water (Australia)
Sydney Water supply over 1.5 billion litres of drinking water to over 5.3 million people every day. Water is supplied from 11 major dams through 13 water delivery systems with:
1.37 Million service connections
12900 miles (20,800 km) mains
Average Pressure 75 psi (52.8m)
82% rigid mains, 85% rigid services (mains to curb stop)
248 reservoirs, 152 pumping stations
9 water filtration plants, Sydney Desalination Plant
655 UARL with SCF calculations to map all pressure zones, supply zones, and distribution systems across 13 water delivery systems
2020 ILI = 1.3
All data reproduced with kind permission of
Sydney Water, Australia

## Slide 56: Case Study 3 – Sydney Water (Australia)
All data reproduced with kind permission of Sydney Water, Australia
Case Study characteristics | 
Zone/System size | 12 – 384,864 service connections
Small Systems | >68% zones have <5,000 service connections
Managed AZP ranges | 21-195 psi (15-137 m)
0

## Slide 57
For some zones, standard UARL equation
over-predicts UARL volumes by up to 63%
SCFs at current operating pressures range from
0.37 – 1.95
Contributes to a complete assessment of all their pressure zones, supply zones, distribution zones and delivery systems -
this will be used for better targeting of further active leakage control
and pressure management activities
Why are these SCFs so varied ?
A wide variety of system/zone size
Mostly rigid mains and service connections
A wide range of operating pressures
How are Sydney Water using SCF calculation results?
For some zones, standard UARL equation
under-predicts UARL volumes by up to 95%
Case Study 3 – Sydney Water (Australia)
All data reproduced with kind permission of Sydney Water, Australia

## Slide 58: Want to achieve similar impact in your water network?
Here are the steps to get you started:

## Slide 59: Leverage smart tech in your network
Understand the context
Define your targets
Deploy the technology
Utilize the insights, implement the interventions
Improve and iterate!

## Slide 60: References
The carbon footprint of desalination: An input-output analysis of seawater reverse osmosis desalination in Australia for 2005–2015, https://doi.org/10.1016/j.desal.2018.12.008
Delaware River Basin Commission Water Audit report - https://www.nj.gov/drbc/library/documents/wateraudits/Assessment_WaterAuditProgram2012-2021_dec2023.pdf
IWA Leakage Emissions Initiative - https://www.leigroup.org/
IWA Water Balance - IWA Water Balance | LEAKSSuite Library
Uncertainty in Water Balances - Random Uncertainty in Water Balance | LEAKSSuite Library
Apparent Losses Guidelines - AL-Guidance-Note-Final-15th-Sep-2016-00000002.pdf
UARL and ILI - UARL and ILI | LEAKSSuite Library
System Correction Factor software – https://www.wlranda.com/software
NRW Reduction training – https://www.wlranda.com/training

## Slide 61: References
A practical approach to increase efficiency & improve feasibility: https://www.flowless.co/knowledge-base/white-paper-reducing-water-losses-a-practical-approach
More than 10 million liters of monthly water savings: https://www.flowless.co/case-studies/water-losses-reduction-in-salfeet
Flowless Octopo: https://www.flowless.co/technology/octopo
Flowless WaterCloud: https://www.flowless.co/technology/watercloud-technology

## Slide 62: Q&A Session
Any questions for Allan, Baker and Kate?
Notes: We will open the floor for questions to address NRW challenges and discuss Flowless' solutions. Additionally, we will conduct a poll to assess the current NRW status and identify the technologies or approaches being used. Original Content: Open the floor for questions from attendees, addressing their specific concerns about NRW challenges and how Flowless' technology can provide solutions. Conduct a poll on the current NRW status across utilities and what technologies or approaches they’re currently using.

## Slide 63: Thank You!
Let us know what you would like to see in future webinars
Follow the link below, or scan the QR code to complete the short survey
https://s.zoom.us/m/bPlTRphyO
or click on the link in the follow-up email which will also include links to the recording